## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 7403 | 7400 | 5750 | 2100 | 1653 | 22.11% | 22.33%
AC-2 | DINING A | 2500 | 3022 | 1950 | 2401 | 550 | 621 | 22% | 20.55%
AC-3 | DINING B | 4920 | 5004 | 3820 | 3865 | 1100 | 1139 | 22.36% | 22.76%
AC-4 | PLAY AREA | 2000 | 2018 | 1560 | 1603 | 440 | 415 | 22% | 20.56%
AC-5 | BOH | 1200 | 1246 | 960 | 1018 | 240 | 228 | 20% | 18.3%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1935
EF-2 | HOOD 2 | [10 empty] | 701 | 639
EF-3 | RESTOOMS | [12 empty] | 500 | 524
EF-4 | HOOD 3 | [10 empty] | 701 | 699
TOTALS |  | 20120 | 18693 | 15690 | 14637 | 4430 | 4056 |  |  | 0 | 0 | 3314 | 3273 | 500 | 524
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4430 | 4056 |  | FRONT |  | 0.0137 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3814 | 3797 |  | SIDE |  | 0.0043 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 616 | 259 |  | REAR |  | 0.0028 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0069333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390