## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
FCU-1 | EXAM ROOMS | 1828 | 1797 | 1543 | 1797 | 285 | 0 | 15.59% | 0%
FCU-2 | FRONT OF HOUSE | 1200 | 1228 | 1015 | 1228 | 185 | 0 | 15.42% | 0%
FCU-3 | TREATMENT | 1200 | 1134 | 960 | 902 | 240 | 232 | 20% | 20.46%
ERV-1 | FCU-1 & FCU-2 |  | 0
ERV-3 | FCU-3 |  | 448
EF-2 | TOILET 119 | [12 empty] | 80 | 0
EF-2 | TOILET 111 | [12 empty] | 110 | 0
TOTALS |  | 4228 | 4607 | 3518 | 3927 | 710 | 232 |  |  | 0 | 0 | 0 | 0 | 190 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 710 | 232 |  | FRONT |  | -0.0023 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 190 | 0 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 520 | 232 |  | REAR |  | 0.0045 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0011 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Restroom exhaust fans are not wired up. Front door is located in hallway of commercial space.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0