## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3300 | 3274 | 0 | 0 | 3300 | 3274 | 100% | 100%
RTU-2 | KITCHEN | 3300 | 3234 | 0 | 0 | 3300 | 3234 | 100% | 100%
RTU-3 | DINING | 3300 | 3244 | 1400 | 1364 | 1900 | 1880 | 57.58% | 57.95%
RTU-4 | DINING | 3300 | 3334 | 1400 | 1380 | 1900 | 1954 | 57.58% | 58.61%
EF-1 | KITCHEN HD 1 | [10 empty] | 1500 | 1497
EF-2 | KITCHEN HD 2 | [10 empty] | 1700 | 1674
EF-3 | KITCHEN HD 3 | [10 empty] | 2125 | 2121
EF-4 | KITCHEN HD 4 | [10 empty] | 2125 | 2134
EF-5 | KITCHEN HD 5&6 | [10 empty] | 1800 | 1745
EF-6 | RESTROOM | [12 empty] | 500 | 0
TOTALS |  | 13200 | 13086 | 2800 | 2744 | 10400 | 10342 |  |  | 0 | 0 | 9250 | 9171 | 500 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 10400 | 10342 |  | FRONT |  | 0.002 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 9750 | 9171 |  | SIDE |  | 0.002 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 650 | 1171 |  | REAR |  | 0.004 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0026667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390