## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8000 | 8775 | 6000 | 6943 | 2000 | 1832 | 25% | 20.88%
AC-2 | SIDE DINING | 4000 | 4167 | 3000 | 3250 | 1000 | 917 | 25% | 22.01%
AC-3 | MAIN DINING | 4240 | 4450 | 3040 | 3294 | 1200 | 1156 | 28.3% | 25.98%
AC-4 | PLAY AREA | 1800 | 1922 | 1500 | 1595 | 300 | 327 | 16.67% | 17.01%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1881
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1345
EF-3 | RESTROOM | [12 empty] | 400 | 402
TOTALS |  | 18040 | 19314 | 13540 | 15082 | 4500 | 4232 |  |  | 0 | 0 | 3314 | 3226 | 400 | 402
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4500 | 4232 |  | FRONT |  | 0.021 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3714 | 3628 |  | SIDE |  | 0.019 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 786 | 604 |  | REAR |  | 0.01 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.016667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390