## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6100 | 6099 | 4150 | 4187 | 1950 | 1912 | 31.97% | 31.35%
RTU-2 | KITCHEN | 6200 | 6564 | 4250 | 4591 | 1950 | 1973 | 31.45% | 30.06%
PRV-1 | RESTROOM | [12 empty] | 375 | 406
PRV-2 | GRIDDLE | [10 empty] | 1500 | 1475
PRV-3 | FRYER | [10 empty] | 1500 | 1545
PRV-4 | DISH | [10 empty] | 350 | 343
EF-1A | MOP | [12 empty] | 75 | 71
TOTALS |  | 12300 | 12663 | 8400 | 8778 | 3900 | 3885 |  |  | 0 | 0 | 3350 | 3363 | 450 | 477
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3900 | 3885 |  | FRONT |  | 0.0108 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3800 | 3840 |  | SIDE |  | 0.0029 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 45 |  | REAR |  | 0.0116 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0084333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0