## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 2400 | 2407 | 1850 | 1847 | 550 | 560 | 22.92% | 23.27%
RTU-2 | DINING | 3000 | 3182 | 2250 | 2397 | 750 | 785 | 25% | 24.67%
MUA-1 | KITCHEN HOOD | [8 empty] | 2718 | 2536
EF-1 | HD-2 FRYER | [10 empty] | 3600 | 3630
EF-2 | MENS RESTROOM | [12 empty] | 100 | 0
EF-3 | WOMENS RESTROOM | [12 empty] | 100 | 0
TOTALS |  | 5400 | 5589 | 4100 | 4244 | 1300 | 1345 |  |  | 2718 | 2536 | 3600 | 3630 | 200 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4018 | 3881 |  | FRONT |  | 0.0021 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3800 | 3630 |  | SIDE |  | 0.0014 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 218 | 251 |  | REAR |  | 0.0012 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0015667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE | [9 empty] | 1950 |  | 3200 |  | -1250