## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 4000 | 4246 | 3000 | 3280 | 1000 | 966 | 25% | 22.75%
RTU-2 | KITCHEN | 5000 | 5230 | 3700 | 3868 | 1300 | 1362 | 26% | 26.04%
FCU-1 | OFFICE |  |  | -40 | -42 | 40 | 42 | #DIV/0! | #DIV/0!
PCU-1 | KITCHEN HDS | [10 empty] | 2048 | 2042
EF-1 | RESTROOM | [12 empty] | 150 | 156
TOTALS |  | 9000 | 9476 | 6660 | 7106 | 2340 | 2370 |  |  | 0 | 0 | 2048 | 2042 | 150 | 156
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2340 | 2370 |  | FRONT |  | 0.0025 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2198 | 2198 |  | SIDE |  | 0.0035 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 142 | 172 |  | REAR |  | 0.0002 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0020667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 1340 | 1404
TOTAL KITCHEN EXHAUST |  | 2048 | 2042
NET AIRFLOW |  | -708 | -638
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0