## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 4000 | 3832 | 3600 | 3366 | 400 | 466 | 10% | 12.16%
RTU-2 | DINING | 3400 | 3374 | 2675 | 2585 | 725 | 789 | 21.32% | 23.38%
MUA-1 | COOKLINE | [8 empty] | 2821 | 2775
EF-1 | HD2 FRYERS | [10 empty] | 1852 | 1909
EF-2 | HD1 GRILLS | [10 empty] | 1662 | 1628
EF-3 | RESTROOM/MOP SINK | [12 empty] | 210 | 200
TOTALS |  | 7400 | 7206 | 6275 | 5951 | 1125 | 1255 |  |  | 2821 | 2775 | 3514 | 3537 | 210 | 200
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3946 | 4030 |  | FRONT |  | 0.019 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3724 | 3737 |  | SIDE |  | NA |  |  | 0 | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 222 | 293 |  | REAR |  | NA | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.019 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
NO SIDE OR REAR ENTRANCE
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0