## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | STORAGE | 1400 | 1334 | 1250 | 1189 | 150 | 145 | 10.71% | 10.87%
RTU-2 | WEST SALES | 2800 | 2821 | 2150 | 2160 | 650 | 661 | 23.21% | 23.43%
RTU-3 | EAST SALES | 2800 | 2781 | 2150 | 2136 | 650 | 645 | 23.21% | 23.19%
RTU-4 | SOUTH SALES | 3500 | 3653 | 2725 | 2897 | 775 | 756 | 22.14% | 20.7%
EF-1 | RESTROOM | [12 empty] | 75 | 63
EF-2 | RESTROOM | [12 empty] | 75 | 74
TOTALS |  | 10500 | 10589 | 8275 | 8382 | 2225 | 2207 |  |  | 0 | 0 | 0 | 0 | 150 | 137
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2225 | 2207 |  | FRONT |  | 0.017 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 150 | 137 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 2075 | 2070 |  | REAR |  | 0.015 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.016 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0