## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | SALES | 6125 | 5773 | 5437 | 5124 | 688 | 649 | 11.23% | 11.24%
RTU-2 | SALES | 3500 | 3363 | 2850 | 2739 | 650 | 624 | 18.57% | 18.55%
RTU-3 | PHARMACY | 1750 | 1697 | 1650 | 1589 | 100 | 108 | 5.714% | 6.364%
RTU-4 | STOCK ROOM | 1050 | 1024 | 950 | 930 | 100 | 94 | 9.524% | 9.18%
EF-1 | LOUNGE | [12 empty] | 300 | 281
EF-2 | MEN RR | [12 empty] | 240 | 227
EF-3 | WOMENS RR | [12 empty] | 240 | 209
EF-4 | OFFICE | [12 empty] | 300 | 276
TOTALS |  | 12425 | 11857 | 10887 | 10382 | 1538 | 1475 |  |  | 0 | 0 | 0 | 0 | 1080 | 993
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1538 | 1475 |  | FRONT |  | 0.004 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1080 | 993 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 458 | 482 |  | REAR |  | - | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.004 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0