## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6150 | 6064 | 4150 | 4126 | 2000 | 1938 | 32.52% | 31.96%
RTU-2 | KITCHEN | 6000 | 5371 | 4000 | 3651 | 2000 | 1720 | 33.33% | 32.02%
PRV-1 | RESTROOMS | [12 empty] | 375 | 372
PRV-2 | HD1 GRILL | [10 empty] | 1500 | 1475
PRV-3 | HD2 FRYER | [10 empty] | 1500 | 1567
PRV-4 | CONDENSATE | [10 empty] | 350 | 339
EF-1 | MOP ROOM | [12 empty] | 75 | 72
EF-2 | EMPLOYER | [12 empty] | 75 | 77
TOTALS |  | 12150 | 11435 | 8150 | 7777 | 4000 | 3658 |  |  | 0 | 0 | 3350 | 3381 | 525 | 521
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 4000 | 3658 |  | FRONT |  | -0.004 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3875 | 3902 |  | SIDE |  | -0.032 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 125 | -244 |  | REAR |  | -0.001 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.012333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
[1] Pressure on the side door reading higher a negagtive due to wind gusting on the side of the building
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0