## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3300 | 3257 | 2230 | 2197 | 1070 | 1060 | 32.42% | 32.55%
RTU-2 | KITCHEN | 4600 | 4375 | 2175 | 1987 | 2425 | 2388 | 52.72% | 54.58%
FCU-1 | OFFICE |  |  |  |  | 40 | 41 | #DIV/0! | #DIV/0!
KEF-1 | HD1 GRILL | [10 empty] | 700 | 711
KEF-2 | HD2 GRILL | [10 empty] | 700 | 678
KEF-3 | HD3 FRYER | [10 empty] | 700 | 719
KEF-4 | HD4 FRYER | [10 empty] | 700 | 694
EF-1 | RESTROOMS | [12 empty] | 300 | 290
TOTALS |  | 7900 | 7632 | 4405 | 4184 | 3535 | 3489 |  |  | 0 | 0 | 2800 | 2802 | 300 | 290
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3535 | 3489 |  | FRONT |  | 0.0137 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3100 | 3092 |  | SIDE |  | 0.0093 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 435 | 397 |  | REAR |  | 0.0068 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0099333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2465 | 2429
TOTAL KITCHEN EXHAUST |  | 2800 | 2802
NET AIRFLOW |  | -335 | -373
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0