## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8500 | 8820 | 6500 | 6729 | 2000 | 2091 | 23.53% | 23.71%
AC-2 | DINING, SERVING | 2830 | 2748 | 2080 | 2009 | 750 | 739 | 26.5% | 26.89%
AC-3 | DINING | 4000 | 4163 | 3000 | 3184 | 1000 | 979 | 25% | 23.52%
AC-4 | DINING | 2765 | 2767 | 2165 | 2157 | 600 | 610 | 21.7% | 22.05%
AC-5 | PLAY AREA | 1800 | 1801 | 1500 | 1480 | 300 | 321 | 16.67% | 17.82%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1915
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1304
EF-3 | RESTROOM | [12 empty] | 400 | 421
TOTALS |  | 19895 | 20299 | 15245 | 15559 | 4650 | 4740 |  |  | 0 | 0 | 3314 | 3219 | 400 | 421
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4650 | 4740 |  | FRONT |  | 0.0065 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3714 | 3640 |  | SIDE |  | 0.0054 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 936 | 1100 |  | REAR |  | 0.0073 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0064 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390