## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3000 | 3115 | 2250 | 2372 | 750 | 743 | 25% | 23.85%
RTU-2 | KITCHEN | 3000 | 2967 | 2250 | 2186 | 750 | 781 | 25% | 26.32%
MUA-1 | HD1 / HD3 | [8 empty] | 1650 | 1647
EF-1 | HD1 GRILL | [10 empty] | 1120 | 1121
EF-2 | HD2 OVN | [10 empty] | 600 | 614
EF-3 | HD3 FRYER | [10 empty] | 833 | 818
EF-4 | RESTROOM | [12 empty] | 75 | 79
TOTALS |  | 6000 | 6082 | 4500 | 4558 | 1500 | 1524 |  |  | 1650 | 1647 | 2553 | 2553 | 75 | 79
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3150 | 3171 |  | FRONT |  | 0.0073 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2628 | 2632 |  | SIDE |  | 0.01 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 522 | 539 |  | REAR |  | 0.0105 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0092667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0