## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 6000 | 6000 | 4500 | 4505 | 1500 | 1495 | 25% | 24.92%
RTU-2 | DINING | 5000 | 5000 | 3750 | 3860 | 1250 | 1140 | 25% | 22.8%
RTU-3 | DINING | 2000 | 2000 | 1500 | 1477 | 500 | 523 | 25% | 26.15%
RTU-4 | DINING | 2000 | 2000 | 1500 | 1493 | 500 | 507 | 25% | 25.35%
RTU-5 | DINING | 5000 | 5000 | 3750 | 4418 | 1250 | 582 | 25% | 11.64%
MAU-1 | HOOD | [8 empty] | 1302 | 1302
MAU-2 | HOOD | [8 empty] | 1242 | 1242
MAU-3 | HOOD | [8 empty] | 1034 | 1034
KEF-1 | HOOD 1 - LEFT | [10 empty] | 2475 | 2493
KEF-2 | HOOD 1 - RIGHT | [10 empty] | 2138 | 3452
KEF-3 | HOOD 2 | [10 empty] | 1650 | 2738
KEF-4 | DISH | [10 empty] | 800 | 866
TOTALS |  | 20000 | 20000 | 15000 | 15753 | 5000 | 4247 |  |  | 3578 | 3578 | 7063 | 9549 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 8578 | 7825 |  | FRONT | [10 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 7063 | 9549 |  | SIDE |  | -0.024 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1515 | -1724 |  | REAR | [10 empty] | FALSE
[5 empty] | AVERAGE |  | -0.024 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
400 CFM / TON 25% FOR OA - SUPPLY TOTALS NOT READ OUT. THESE SERVE AS PLACEHOLDERS AND TO CALCULATE APPROPRIATE OUTSIDE AIR TARGETS.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0