## Report Sheet
STORE #: | 4127 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | NORWALK ,OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (FRYER) - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-05-23 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | DYLAN CRISMAN | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | 48HCED09A3M5-6F4J0 | 0922P97642 | RTU-1 | KITCHEN | 500 | 1001 | 0 | 0 |  | 1732 | 1729 | 879 | 875 | NL | 209.3 | 209.9 | 3 | 9.2 | 5.2 | 5.3 | 1.8193 | 1.8596 | 2.215%
YORK | 48HCED11A2M5-6F4J0 | 0722P96420 | RTU-2 | DINING | 1000 | 1924 | 1000 | 1015 |  | 1706 | 1698 | 925 | 921 | NL | 209 | 208.8 | 3 | 9.2 | 6.86 | 6.66 | 2.3967 | 2.3246 | -3.008%
CAPTIVE AIRE | A1-D.250-15D | 5085703 | MUA-1 | HOOD 1 | 1950 | 2136 | 1700 | 1751 | No | 1538 | 1329 | 1538 | 1329 | 2 | 115 | 69 | 3 | 5.48 | 6.4 | 4.9 | 1.2303 | 0.56518 | -54.06%
CAPTIVE AIRE | DU240HFA | 5085703 | EF-1 | HOOD 1 | 3200 | 3110 | 2450 | 2446 | No | 817 | 625 | 817 | 625 | 3 | 154 | 121 | 3 | 10.2 | 5.1 | 4.5 | 1.3129 | 0.91021 | -30.67%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 5061 | 2700 | 2766 |  | FRONT DOOR |  | -0.008 |  |  | INITIAL | 6.7593 | 5061
|  |  | TOTAL EXHAUST |  | 3350 | 3260 | 2600 | 2596 |  | BACK DOOR |  | 0.0104 |  |  | FINAL | 5.6596 | 2766
|  |  | NET AIRFLOW |  | 100 | 1801 | 100 | 170 |  | AVERAGE |  | 0.0012 |  |  | ∆ | -1.0996 | -2295
Issue List
Unit # | Description
RTU-1/RTU-2 | RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU-2 | RTU-2 Alarm on honeywell reading: (OA SENS T ERR).

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not running / MUA is not running. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.