## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-R2-1 | DINING | 2000 | 2128 | 1600 | 1710 | 400 | 418 | 20% | 19.64%
AHU-R2-2 | DINING | 1400 | 1449 | 1120 | 1186 | 280 | 263 | 20% | 18.15%
AHU-R2-3 | KITCHEN | 2950 | 3112 | 2360 | 2514 | 590 | 598 | 20% | 19.22%
MUA-1 | KITCHEN HOOD | [8 empty] | 1950 | 2003
EF-1 | KITCHEN HOOD | [10 empty] | 3200 | 3203
EF-2-1 | RESTROOM | [12 empty] | 75 | 192
EF-2-2 | RESTROOM | [12 empty] | 75 | 183
EF-3 | RESTROOM | [12 empty] | 50 | 168
EF-4 | RESTROOM | [12 empty] | 50 | 160
TOTALS |  | 6350 | 6689 | 5080 | 5410 | 1270 | 1279 |  |  | 1950 | 2003 | 3200 | 3203 | 250 | 703
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3220 | 3282 |  | FRONT |  | -0.036 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3450 | 3906 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -230 | -624 |  | REAR | [10 empty] | FALSE
[5 empty] | AVERAGE |  | -0.036 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
[1] With all systems off, building pressure measured at -0.032".
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 20X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250