## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | CENTER SALES | 17500 | 17771 | 15450 | 15830 | 2050 | 1941 | 11.71% | 10.92%
RTU-2 | EAST SALES | 20800 | 19027 | 18180 | 16504 | 2620 | 2523 | 12.6% | 13.26%
RTU-3 | WEST SALES | 8750 | 7596 | 7702 | 6536 | 1048 | 1060 | 11.98% | 13.95%
RTU-4 | PHARMACY | 1600 | 1663 | 1600 | 1663 | 0 | 0 | 0% | 0%
RTU-5 | BAKERY | 2450 | 2448 | 2180 | 2167 | 270 | 281 | 11.02% | 11.48%
RTU-6 | MEZZANINE | 3850 | 3693 | 3400 | 3254 | 450 | 439 | 11.69% | 11.89%
EF-4 | FRONT RR | [12 empty] | 600 | 648
EF-5 | MEAT DEPARTMENT | [12 empty] | 0 | 0
EF-1 | BAKE OVEN | [12 empty] | 675 | 356
EF-3 | DISH WASHER | [12 empty] | 0 | 0
EF-H | REAR RESTROOM | [12 empty] | 400 | 385
EF-1A | HD-2 | [10 empty] | 967 | 967
EF-2 | HD- 1 | [10 empty] | 2321 | 2321
TOTALS |  | 54950 | 52198 | 48512 | 45954 | 6438 | 6244 |  |  | 0 | 0 | 3288 | 3288 | 1675 | 1389
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 6438 | 6244 |  | FRONT |  | -0.003 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 4963 | 4677 |  | SIDE |  | -0.001 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 1475 | 1567 |  | REAR |  | -0.002 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.002 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
[1] RTU-1 WAS TO SERVE EASTERN SECTION OF STORE, DESIGN VALUES WERE SWITCHED SINCE UNITS WERE THE SAME TONNAGE. [2] UNABLE TO 100% VERIFY BUILDING WAS SEALED DURING PRESSURE TESTING DUE TO BEING PEAK HOURS. [3] IF NEGATIVE THEN COMPRESSOR ROOM IS THE SOURCE.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0