## Report Sheet
STORE #: | 4322 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | AUSTINTOWN, OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 410258 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | JORDAN BEST | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
BRYANT | 580JP09D180A2A0ADA | 3522P37637 | RTU-1 | KITCHEN | 500 | 876 | 0 | 876 |  | 1706 | 1706 | 749 | 749 | NL | 209.4 | 209.4 | 3 | 6.7 | 4.78 | 4.78 | 1.6732 | 1.6732 | 0%
BRYANT | 580JP12D224A2A0ADA | 2622P31773 | RTU-2 | DINING | 1000 | 791 | 1000 | 791 |  | 1761 | 1761 | 864 | 864 | NL | 208.1 | 208.1 | 3 | 9.2 | 6.5 | 6.5 | 2.2611 | 2.2611 | 0%
CAPTIVE AIRE | A.1-D.250-15D | 5432961 | MUA-1 | HOOD 1 | 1950 | 1715 | 1700 | 1715 | No | 1905 | 1905 | 1905 | 1905 | 2 | 210 | 210 | 3 | 5.48 | 4.1 | 4.1 | 1.4393 | 1.4393 | 0%
CAPTIVE AIRE | DU240HFA | 5432961 | EF-1 | HOOD 1 | 3200 | 2980 | 2450 | 2592 | No | 1305 | 1160 | 1305 | 1160 | 3 | 210.5 | 210.2 | 3 | 9.2 | 6.4 | 5.8 | 2.252 | 2.038 | -9.504%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 3382 | 2700 | 3382 |  | FRONT DOOR |  | 0.0012 |  |  | INITIAL | 7.6256 | 3382
|  |  | TOTAL EXHAUST |  | 3350 | 3130 | 2600 | 2742 |  | BACK DOOR |  | 0.0004 |  |  | FINAL | 7.4116 | 5974
|  |  | NET AIRFLOW |  | 100 | 252 | 100 | 640 |  | AVERAGE |  | 0.0008 |  |  | ∆ | 0.21404 | -2592
Issue List
Unit # | Description
Select from drop down list
RTU-1 | RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU2 | RTU / OA Damper / Outside air damper is not functional and OA could not be set.

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not running / MUA is not running. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.