## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
EH-1 | Entrance | 1500 | 1560
RTU-1 | SALES | 6125 | 6270 | 5437 | 5632 | 688 | 638 | 11.23% | 10.18%
RTU-2 | SALES | 4375 | 3040 | 3562 | 2489 | 813 | 551 | 18.58% | 18.12%
RTU-3 | PHARMACY | 1750 | 1843 | 1650 | 1736 | 100 | 107 | 5.714% | 5.806%
RTU-4 | STOCK ROOM | 1050 | 1113 | 950 | 1007 | 100 | 106 | 9.524% | 9.524%
EF-1 | LOUNGE | [12 empty] | 300 | 291
EF-2 | MENS RR | [12 empty] | 240 | 266
EF-3 | WOMENS RR | [12 empty] | 240 | 321
EF-4 | OFFICE | [12 empty] | 300 | 239
EF-5 | PHOTO | [12 empty] | 750 | 0
TOTALS |  | 13300 | 12266 | 11599 | 10864 | 1701 | 1402 |  |  | 0 | 0 | 0 | 0 | 1830 | 1117
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | TRUE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 1701 | 1402 |  | FRONT |  | 0.005 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1830 | 1117 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -129 | 285 |  | REAR |  | 0.003 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.004 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0