## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3352 | 2400 | 2349 | 1000 | 1003 | 29.41% | 29.92%
RTU-2 | DINING | 4000 | 4003 | 2850 | 2841 | 1150 | 1162 | 28.75% | 29.03%
EF-1 | KITCHEN HOOD | [10 empty] | 1900 | 1814
EF-2 | RESTROOM | [12 empty] | 150 | 143
TOTALS |  | 7400 | 7355 | 5250 | 5190 | 2150 | 2165 |  |  | 0 | 0 | 1900 | 1814 | 150 | 143
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2150 | 2165 |  | FRONT |  | 0 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2050 | 1957 |  | SIDE |  | 0.0048 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 208 |  | REAR |  | 0.0028 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0025333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 7 16X16 | [7 empty] | 0 |  | 1900 |  | -1900