## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  | 3000 | 3007 | 2500 | 2516 | 500 | 491 | 16.67% | 16.33%
RTU-2 |  | 3000 | 2971 | 2500 | 2490 | 500 | 481 | 16.67% | 16.19%
MUA-1 | [10 empty] | 0
EF-1 | [12 empty] | 1846
EF-2 | [12 empty] | 1137
EF-3 | [12 empty] | 245
TOTALS |  | 6000 | 5978 | 5000 | 5006 | 1000 | 972 |  |  | 0 | 0 | 0 | 3228 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 1000 | 972 |  | FRONT |  | -0.055 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 0 | 3228 |  | SIDE |  | -0.0515 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1000 | -2256 |  | REAR |  | -0.045 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.0505 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0