## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
DOAS-1 | KITCHEN | 3000 | 2896 | 0 | 0 | 3000 | 2896 | 100% | 100%
RTU-2 | DINING | 4000 | 4053 | 2000 | 2032 | 2000 | 2021 | 50% | 49.86% |  |  |  |  | 1000 | 964
AC-1 | OFFICE |  |  |  |  | 40 | 36 | N/A | N/A
KEF-1 | HD1 GRILL-SM | [10 empty] | 700 | 682
KEF-2 | HD2 GRILL-LG | [10 empty] | 1050 | 1082
KEF-3 | HD3 FRY-CHK | [10 empty] | 642 | 624
KEF-4 | HD4 FRYER-FRY | [10 empty] | 642 | 665
TX-1 | RESTROOMS | [12 empty] | 300 | 301
TOTALS |  | 7000 | 6949 | 2000 | 2032 | 5040 | 4953 |  |  | 0 | 0 | 3034 | 3053 | 1300 | 1265
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 5040 | 4953 |  | FRONT |  | 0.003 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 4334 | 4318 |  | SIDE |  | 0.006 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 706 | 635 |  | REAR |  | 0.0031 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0040333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 3000 | 2896
TOTAL KITCHEN EXHAUST |  | 3034 | 3053
NET AIRFLOW |  | -34 | -157
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0