## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN |  | 4089 |  | 3079 |  | 1010 | #DIV/0! | 24.7%
RTU-2 | DINING |  | 3032 | 0 | 2453 |  | 579 | #DIV/0! | 19.1%
MUA-1 | KITCHEN HD | [9 empty] | 791
KEF-1 | KITCHEN HD | [11 empty] | 894
KEF-2 | KITCHEN HD | [11 empty] | 889
KEF-3 | KITCHEN HD | [11 empty] | 524
EF-2 | RESTROOM | [13 empty] | 0
TOTALS |  | 0 | 7121 | 0 | 5532 | 0 | 1589 |  |  | 0 | 791 | 0 | 2307 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 0 | 2380 |  | FRONT |  | -0.0012 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 0 | 2307 |  | SIDE |  | -0.0009 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 0 | 73 |  | REAR |  | -0.0059 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0026667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0