Factory 52 Test and Balance

Scope of work includes (3) Roof top units, (6) Fan coil units, (2) exhaust fans, and (4) Make up air units, and all associated air devices. All systems are successfully balance to within 10% utilizing local speed drives or via pulley reconfiguration. The following should be noted in reflection of the final results:

- MUA fans were only able to be measured in temporary test mode at 30hz. Final setpoints are recorded for each respective fan.

- FCU-1 grilles were not installed but the unit total was set.