## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5500 | 5767 | 3795 | 3914 | 1705 | 1853 | 31% | 32.13%
RTU-2 | KITCHEN | 5500 | 5332 | 3795 | 3494 | 1705 | 1838 | 31% | 34.47%
EF-1 | MOP SINK | [12 empty] | 75 | 0
PRV1 | RESTROOMS | [12 empty] | 375 | 0
PRV2 | GRIDDLE HD-1 | [10 empty] | 1500 | 1597
PRV3 | FRYER HD-2 | [10 empty] | 1500 | 1614
PRV4 | DISH HOOD | [10 empty] | 350 | 0
TOTALS |  | 11000 | 11099 | 7590 | 7408 | 3410 | 3691 |  |  | 0 | 0 | 3350 | 3211 | 450 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | TRUE | FALSE
TOTALS |  |  | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3410 | 3691 |  | FRONT |  | 0.01" | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3800 | 3211 |  | SIDE |  | 0.009" |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -390 | 480 |  | REAR |  | 0.01" | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.01 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
[1] Balanced RTU outside air to high end of design to accommodate PRV-1, PRV-4, and EF-1A exhaust should these fans be repaired. Recommend PRV-4 be tied into dishwasher operation to keep building pressure positive if all fans are repaired.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0