## Report Sheet
STORE #: | 3821 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | MENTOR, OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-05-06 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | JORDAN BEST | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | J102NA8R2B5EAA2A2 | N2K0232323 | RTU-1 | KITCHEN | 500 | 265 | 0 | 0 |  | 1757 | 1757 | 980 | 980 | 3 | 213.6 | 213.6 | 3 | 8.3 | 7.13 | 7.13 | 2.5458 | 2.5458 | 0%
YORK | ZJ090N18R2B5EAA2A2 | N2K0247571 | RTU-2 | DINING | 1000 | 548 | 1000 | 973 |  | 1743 | 1743 | 945 | 945 | 3 | 213.2 | 213.2 | 3 | 8.3 | 7.81 | 7.81 | 2.7834 | 2.7834 | 0%
CAPTIVE AIRE | D.250-G10 | 4457725 | MUA-1 | HOOD 1 | 1950 | 1857 | 1700 | 1694 | No | 1770 | 1778 | 1087 | 990 | 2 | 212 | 212 | 3 | 5.3 | 3.03 | 2.76 | 1.0738 | 0.97811 | -8.911%
CAPTIVE AIRE | NCA24HPFA | 4457725 | EF-1 | HOOD 1 | 3200 | 3223 | 2450 | 2673 | No | 1757 | 1788 | 960 | 798 | 2 | 213 | 213 | 3 | 5.38 | 4.07 | 3.36 | 1.4492 | 1.1964 | -17.44%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 2670 | 2700 | 2667 |  | FRONT DOOR |  | -0.0182 |  |  | INITIAL | 7.8522 | 2670
|  |  | TOTAL EXHAUST |  | 3350 | 3373 | 2600 | 2823 |  | BACK DOOR |  | -0.0077 |  |  | FINAL | 7.5037 | 5340
|  |  | NET AIRFLOW |  | 100 | -703 | 100 | -156 |  | AVERAGE |  | -0.01295 |  |  | ∆ | 0.34849 | -2670
Issue List
Unit # | Description
Select from drop down list
MUA | MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
RTU-2 | RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
798

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not running / MUA is not running. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.