## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 2400 | 2464 | 1300 | 1311 | 1100 | 1153 | 45.83% | 46.79%
RTU-2 | KITCHEN | 4700 | 4724 | 2200 | 2188 | 2500 | 2536 | 53.19% | 53.68%
FCU-1 | MANAGERS OFFICE |  |  |  |  | 40 | 41 | #DIV/0! | #DIV/0!
KEF-1 | HD1 | [10 empty] | 700 | 724
KEF-2 | HD2 | [10 empty] | 700 | 736
KEF-3 | HD3 | [10 empty] | 700 | 769
KEF-4 | HD4 | [10 empty] | 700 | 728
EF-1 | RESTROOMS | [12 empty] | 300 | 304
TOTALS |  | 7100 | 7188 | 3500 | 3499 | 3640 | 3730 |  |  | 0 | 0 | 2800 | 2957 | 300 | 304
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3640 | 3730 |  | FRONT |  | 0.0037 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3100 | 3261 |  | SIDE |  | 0.0079 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 540 | 469 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0058 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2540 | 2577
TOTAL KITCHEN EXHAUST |  | 2800 | 2957
NET AIRFLOW |  | -260 | -380
UNABLE TO GET ACCURATE OA READING FROM RTU-1/RTU-2 DUE TO OA DAMPER FLUCTUATING. OA IS SET TO STABILIZE BUILDING PRESSURE TEMPORARILY. BUILDING PRESSURE IS STILL FLUCTUATING BETWEEN POSITIVE 0.0057" AND NEGATIVE -0.0074" AFTER SEVERAL READINGS.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0