## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING I & RR | 3000 | 3061 | 2500 | 2537 | 500 | 524 | 16.67% | 17.12%
RTU-2 | DINING II & COUNTER | 3000 | 3039 | 2500 | 2502 | 500 | 537 | 16.67% | 17.67%
DOAS-1 | KITCHEN | 2450 | 2405 | 0 | 0 | 2450 | 2405 | 100% | 100%
KEF-1 | GRIDDLE | [10 empty] | 1600 | 1588
KEF-2 | FRYER | [10 empty] | 1046 | 1110
EF-1 | RR | [12 empty] | 225 | 246
EF-2 | RR | [12 empty] | 225 | 247
TOTALS |  | 8450 | 8505 | 5000 | 5039 | 3450 | 3466 |  |  | 0 | 0 | 2646 | 2698 | 450 | 493
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3450 | 3466 |  | FRONT |  | 0.0048 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3096 | 3191 |  | SIDE |  | 0.0066 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 354 | 275 |  | REAR |  | 0.0143 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0085667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0