## Report Sheet
STORE #: | 2527 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | HIGHLAND HEIGHTS, OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-06-05 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | JORDAN BEST | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
TRANE |  |  | RTU-1 | KITCHEN | 500 | 412 | 0 | 0 |  | 1743 | 1743 | 680 | 680 | 1 | 215.4 | 215.4 | 3 | 4 | 2.91 | 2.91 | 1.0478 | 1.0478 | 0%
TRANE | YHC092F3RHA0RTP | 153210909L | RTU-2 | DINING | 1000 | 0 | 1000 | 964 |  | 1.67 | 1.67 | 1.67 | 1.67 | 3 | 212.3 | 212.3 | 3 | 8.5 | 2.07 | 2.07 | 0.73462 | 0.73462 | 0%
CAPTIVE AIRE | A1-D.250-G10 | 2344220 | MUA-1 | HOOD 1 | 1950 | 1525 | 1700 | 1525 | No | 1742 | 1742 | 1109 | 1109 | 2 | 210.3 | 210.3 | 3 | 6.8 | 3.49 | 3.49 | 1.2269 | 1.2269 | 0%
CAPTIVE AIRE | NA | 2344220 | EF-1 | HOOD 1 | 3200 | 2653 | 2450 | 2653 | No | 1753 | 1753 | 822.8 | 822.8 | 2 | 209.6 | 209.6 | 3 | 6.8 | 3.99 | 3.99 | 1.398 | 1.398 | 0%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 1937 | 2700 | 2489 |  | FRONT DOOR |  | -0.0684 |  |  | INITIAL | 4.4073 | 1937
|  |  | TOTAL EXHAUST |  | 3350 | 2803 | 2600 | 2803 |  | BACK DOOR |  | -0.0578 |  |  | FINAL | 4.4073 | 2489
|  |  | NET AIRFLOW |  | 100 | -866 | 100 | -314 |  | AVERAGE |  | -0.0631 |  |  | ∆ | 0 | 552
Issue List
Unit # | Description
Select from drop down list
MUA | MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA | MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
EF-1 | Missing 1 hood filter, covered opening to best ability while reading.
RTU-1 | RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU-2 | RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not running / MUA is not running. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.