## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3800 | 3685 | 3050 | 2895 | 750 | 790 | 19.74% | 21.44%
RTU-2 | DINING | 3800 | 3814 | 3050 | 3043 | 750 | 771 | 19.74% | 20.21%
MUA-1 | KITCHEN HOOD | [8 empty] | 1300 | 1294
EF-1 | KITCHEN HOOD | [10 empty] | 2550 | 2595
EF-2 | RESTROOM | [12 empty] | 200 | 201
TOTALS |  | 7600 | 7499 | 6100 | 5938 | 1500 | 1561 |  |  | 1300 | 1294 | 2550 | 2595 | 200 | 201
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2800 | 2855 |  | FRONT |  | 0.0056 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2750 | 2796 |  | SIDE |  | 0.0074 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 50 | 59 |  | REAR |  | 0.0083 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0071 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 165X9 |  | 1300 |  | 2550 |  | -1250