## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3200 | 3265 | 2200 | 2181 | 1000 | 1084 | 31.25% | 33.2%
RTU-2 | KITCHEN | 4900 | 4242 | 2400 | 1687 | 2500 | 2555 | 51.02% | 60.23%
FCU-1 | OFFICE |  |  |  |  | 40 | 37 | #DIV/0! | #DIV/0!
KEF-1 | HD1 GRILL | [10 empty] | 700 | 691
KEF-2 | HD2 GRILL | [10 empty] | 700 | 707
KEF-3 | HD3 FRYER | [10 empty] | 700 | 716
KEF-4 | HD4 FRYERS | [10 empty] | 700 | 728
EF-1 | RESTROOMS | [12 empty] | 300 | 525
TOTALS |  | 8100 | 7507 | 4600 | 3868 | 3540 | 3676 |  |  | 0 | 0 | 2800 | 2842 | 300 | 525
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3540 | 3676 |  | FRONT |  | 0.005 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3100 | 3367 |  | SIDE |  | 0.003 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 440 | 309 |  | REAR |  | 0.004 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.004 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2500 | 2555
TOTAL KITCHEN EXHAUST |  | 2800 | 2842
NET AIRFLOW |  | -300 | -287
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0