## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6150 | 5908 | 4400 | 4119 | 1750 | 1789 | 28.46% | 30.28%
RTU-2 | KITCHEN | 6225 | 5849 | 4525 | 4102 | 1700 | 1747 | 27.31% | 29.87%
PRV-1 | RESTROOM | [12 empty] | 300 | 285
PRV-2 | HD1 GRIDDLE | [10 empty] | 1500 | 1579
PRV-3 | HD2 FRYER | [10 empty] | 1500 | 1607
EF-1A(X2) | EMP. RR/MOP RM. | [12 empty] | 150 | 142
TOTALS |  | 12375 | 11757 | 8925 | 8221 | 3450 | 3536 |  |  | 0 | 0 | 3000 | 3186 | 450 | 427
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3450 | 3536 |  | FRONT |  | 0.01 | [8 empty] | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 3450 | 3613 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 0 | -77 |  | REAR |  | 0.02 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.015 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
READINGS ARE WITHIN ALLOWABLE TOLERANCE IN CUMMULATIVE READING ERROR.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0