## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | SALES | 10300 | 9324 | 8500 | 7418 | 1800 | 1906 | 17.48% | 20.44%
RTU-2 | SALES | 10300 | 11077 | 8500 | 9220 | 1800 | 1857 | 17.48% | 16.76%
RTU-3 | SALES | 10300 | 9950 | 8500 | 8118 | 1800 | 1832 | 17.48% | 18.41%
RTU-4E | PHARMACY & FT. MEZZ OFFICE | 1500 | 1438 | 1050 | 983 | 450 | 455 | 30% | 31.64%
RTU-5 | SALES | 10300 | 10078 | 8500 | 8204 | 1800 | 1874 | 17.48% | 18.59%
RTU-6 | VESTIBULE | 3400 | 0 | 3000 | 0 | 400 | 0 | 11.76% | #DIV/0!
RTU-7 | DOCK | 4375 | 4551 | 3475 | 3629 | 900 | 922 | 20.57% | 20.26%
MAU | DELI HOODS | [8 empty] | 2320 | 2207
EF-1 | DELI PREP | [10 empty] | 2500 | 2274
EF-2 | DELI PREP | [10 empty] | 2900 | 2968
EF-3 | SEAFOOD | [10 empty] | 800 | 0
EF-5 | RACK OVEN | [10 empty] | 900 | 859
EF-6 | UNISEX RR | [12 empty] | 500 | 0
EF-7 | STORAGE | [12 empty] | 400 | 0
EF-8 | SMOKING ROOM (ABANDONED) | [13 empty] | 0
EF-9 | MEN RESTROOM | [13 empty] | 214
TOTALS |  | 50475 | 46418 | 41525 | 37572 | 8950 | 8846 |  |  | 2320 | 2207 | 7100 | 6101 | 900 | 214
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 11270 | 11053 |  | FRONT |  | 0.004 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 8000 | 6315 |  | SIDE |  | NA |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 3270 | 4738 |  | REAR |  | NA | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.004 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0