## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | BAR DINING | 4400 | 4392 | 3350 | 3333 | 1050 | 1059 | 23.86% | 24.11%
RTU-2 | WAITING DINING | 4400 | 4492 | 3350 | 3527 | 1050 | 965 | 23.86% | 21.48%
RTU-3 | KITCHEN | 4400 | 4327 | 3375 | 3263 | 1025 | 1064 | 23.3% | 24.59%
MUA-1 | COOKLINE | [8 empty] | 4880 | 4757
EF-1 | HOOD 1 | [10 empty] | 2205 | 2315
EF-2 | HOOD 2 | [10 empty] | 2125 | 2159
EF-3 | HOOD 3 | [10 empty] | 1480 | 1661
EF-4 | HOOD 4 | [10 empty] | 1050 | 1057
EF-5 | RESTROOM | [12 empty] | 450 | 433
TOTALS |  | 13200 | 13211 | 10075 | 10123 | 3125 | 3088 |  |  | 4880 | 4757 | 6860 | 7192 | 450 | 433
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 8005 | 7845 |  | FRONT |  | 0.0067 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 7310 | 7625 |  | SIDE |  | 0.0103 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 695 | 220 |  | REAR |  | 0.0185 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.011833 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0