## AHU-1
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: AHU-1
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | TWE12043BAA | SF CFM | 3400
Serial Num |  | SF RPM | 765 | HZ
Configuration | HORIZONTAL | RA CFM | 3000
Num PreFilter |  | OA CFM | 400
PreFilter Size |  | RL VOLTAGE | 208
Num PreFilter |  | RL AMPERAGE
PreFilter Size |  | OA Damper Position
|  | Brake Horsepower | 1.21
Motor Data |  | Performance Data
Motor MFG |  |  | Design | Actual
Frame |  | Fan Suction SP
Horsepower | 2 | Fan Discharge SP
Motor RPM |  | Fan Total SP
Phase | 3 | DX Coil PD * |  | *
Rated Voltage | 208 | Pre Filter PD |  | *combined
Rated Amperage | 6.8 | Total ESP | 0.5
Service Factor
DX Coil DB EAT
INDOOR TEMPS |  | DX Coil DB LAT
CURRENT TEMP. |  | DX Coil WB EAT
HUMIDITY |  | DX Coil WB LAT
WETBULB |  | DX Coil Capacity
OUTDOOR TEMPS
CURRENT TEMP.
HUMIDITY
WETBULB
DEWPOINT

## AHU SGRD
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: AHU-1
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
SGRD-1 | 13 | D | 12X6 | 265 |  |  | 0
SGRD-2 | 13 | D | 12X6 | 275 |  |  | 0
SGRD-3 | 13 | D | 12X6 | 265 |  |  | 0
SGRD-4 | 13 | D | 12X6 | 265 |  |  | 0
SGRD-5 | 13 | D | 12X6 | 265 |  |  | 0
SGRD-6 | 13 | D | 12X6 | 265 |  |  | 0
SGRD-7 | 13 | D | 12X6 | 300 |  |  | 0
SGRD-8 | 13 | D | 12X6 | 300 |  |  | 0
SGRD-9 | 13 | D | 12X6 | 300 |  |  | 0
SGRD-10 | 13 | D | 12X6 | 300 |  |  | 0
SGRD-11 | 13 | D | 12X6 | 300 |  |  | 0
SGRD-12 | 13 | D | 12X6 | 300 |  |  | 0
|  |  |  | 3400 |  | 0 | 0

## OAHU-1
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: OAHU-1 |  | Area:
Unit Data |  |  | Test Data
Manufacurer | TRANE |  |  | Design | Actual
Model Number | UCCAG06 |  | SF CFM | 1310
Serial Number |  |  | SF RPM | 2317
Configuration | HORIZONTAL |  | DESIGN HZ | 78
No. Pre Filters / Size | 4 / 20X20X2 |  | RL VOLTAGE | 208
RL AMPERAGE
|  |  | Motor B.H.P. | 1.832
Motor Data |  |  | Performance Data
Motor MFG |  |  |  | Design | Actual
Frame |  |  | Suction S.P.
HP | 3 |  | Discharge S.P.
RPM |  |  | Total SP | 2.85
Phase | 3 |  | DX Coil P.D. | 0.30
Volts | 208 |  | REHEAT P.D. | 0.136
Amps |  |  | Pre Filters P.D. | 0.536
|  |  | Total ESP | 1.75
INDOOR TEMPS |  |  | DX Coil DB EAT
CURRENT TEMP. |  |  | DX Coil DB LAT
HUMIDITY |  |  | DX Coil WB EAT
WETBULB |  |  | DX Coil WB LAT
DX Coil Capacity
OUTDOOR TEMPS
CURRENT TEMP.
HUMIDITY
WETBULB
DEWPOINT

## OAHU SGRD (2)
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset:
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
SGRD-1 | 4 | A | 4 | 10 |  |  | 0
SGRD-2 | 2 | A | 5 | 50 |  |  | 0
SGRD-3 | 20 | B | 4 | 10 |  |  | 0
SGRD-4 | 21 | A | 6 | 50 |  |  | 0
SGRD-5 | 1 | A | 5 | 30 |  |  | 0
SGRD-6 | 22 | A | 4 | 20 |  |  | 0
SGRD-7 | 29 | A | 5 | 40 |  |  | 0
SGRD-8 | 27 | A | 6 | 90 |  |  | 0
SGRD-9 | 25 | A | 5 | 40 |  |  | 0
SGRD-10 | 103 | A | 10 | 220 |  |  | 0
SGRD-11 | CORRIDOR | A | 8 | 170 |  |  | 0
SGRD-12 | 14 | A | 6 | 70 |  |  | 0
SGRD-13 | 13 | E | 16X8 | 210 |  |  | 0
SGRD-14 | 11 | A | 10 | 290 |  |  | 0
|  |  |  | 1300 |  | 0 | 0

## RTU-1
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: RTU-1
Unit Data |  | Test Data
Manufacturer | TRANE |  | Design | Actual
Model Num | OABD108A3 | SF CFM | 2800
Serial Num |  | SF RPM | 2745 | HZ
Configuration | VERTICAL | RA CFM | 2200
Num OA Filters |  | OA CFM | 600
OA Filter Size |  | RL VOLTAGE | 208
Num PreFilter |  | RL AMPERAGE | VERIFY
PreFilter Size |  | OA Damper Position
|  | Brake Horsepower | 1.82
Motor Data |  | Performance Data
Motor MFG |  |  | Design | Actual
Frame |  | Fan Suction SP
Horsepower | 3 | Fan Discharge SP
Motor RPM |  | Fan Total SP | 1.75
Phase | 3 | DX Coil PD * | 0.29 | *
Rated Voltage | 208 | Pre Filter PD |  | *combined
Rated Amperage | 7.2 | Total ESP | 0.5
Service Factor
DX Coil DB EAT
INDOOR TEMPS |  | DX Coil DB LAT
CURRENT TEMP. |  | DX Coil WB EAT
HUMIDITY |  | DX Coil WB LAT
WETBULB |  | DX Coil Capacity
OUTDOOR TEMPS
CURRENT TEMP.
HUMIDITY
WETBULB
DEWPOINT

## RTU SGRD
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: RTU-1
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
SGRD-1 | 11 | A | 10 | 300 |  |  | 0
SGRD-2 | 11 | A | 10 | 300 |  |  | 0
SGRD-3 | 11 | A | 10 | 300 |  |  | 0
SGRD-4 | 11 | A | 10 | 300 |  |  | 0
SGRD-5 | 11 | A | 10 | 400 |  |  | 0
SGRD-6 | 11 | A | 10 | 300 |  |  | 0
SGRD-7 | 11 | A | 10 | 300 |  |  | 0
SGRD-8 | 11 | A | 10 | 300 |  |  | 0
SGRD-9 | 11 | A | 10 | 300 |  |  | 0
|  |  |  | 2800 |  | 0 | 0

## FCU 3-3
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: FCU 3-3 |  | Area: Corridors
Unit Data |  |  |  |  | Test Data
MFG | TRANE |  |  |  |  | Design | Actual
Model Num |  |  |  |  | SA CFM | 535
Serial Num |  |  |  |  | Fan Speed
RL Voltage
Motor Data |  |  |  |  | RL Amperage
Motor MFG |  |  |  |  | Suction ESP
Horsepower |  |  |  |  | Discharge ESP
Motor Rpm |  |  |  |  | Total ESP
Phase | 1 |  |  |  | DX Coil DB EAT
Voltage (rated) | 208 |  |  |  | DX Coil DB LAT
Amperage (rated) |  |  |  |  | DX Coil WB EAT
DX Coil WB LAT
DX Coil Capacity
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
SGRD-1 | 103 | A | 6 | 50 |  |  | 0
SGRD-2 | 103 | A | 8 | 200 |  |  | 0
SGRD-3 | 102 | F | 12X6 | 185 |  |  | 0
SGRD-4 | 104 | A | 6 | 50 |  |  | 0
SGRD-5 | 102 | A | 6 | 50 |  |  | 0
|  |  |  | 535 |  | 535 | 1
#DIV/0!
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU 6-2)
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: FCU 6-2 |  | Area: Supply Office
Unit Data |  |  |  |  | Test Data
MFG | TRANE |  |  |  |  | Design | Actual
Model Num |  |  |  |  | SA CFM | 530
Serial Num |  |  |  |  | Fan Speed
[5 empty] | RL Voltage | 208
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Discharge ESP
Horsepower |  |  |  |  | Total ESP
Motor Rpm |  |  |  |  | DX Coil DB EAT
Phase |  |  |  |  | DX Coil DB LAT
Voltage (rated) | 208 |  |  |  | DX Coil WB EAT
Amperage (rated) |  |  |  |  | DX Coil WB LAT
DX Coil Capacity
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
SGRD-1 | 14 | A | 6 | 100 |  |  | 0
SGRD-2 | 14 | A | 8 | 215 |  |  | 0
SGRD-3 | 14 | A | 8 | 215 |  |  | 0
|  |  |  | 530 |  | 738 | 1.3925
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## FCU 8
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: FCU 8 |  | Area:
Unit Data |  |  |  |  | Test Data
MFG | TRANE |  |  |  |  | Design | Actual
Model Num |  |  |  |  | SA CFM | 715
Serial Num |  |  |  |  | Fan Speed
RL Voltage
Motor Data |  |  |  |  | RL Amperage | 208
Motor MFG |  |  |  |  | Suction ESP
Horsepower |  |  |  |  | Discharge ESP
Motor Rpm |  |  |  |  | Total ESP
Phase |  |  |  |  | DX Coil DB EAT
Voltage (rated) | 208 |  |  |  | DX Coil DB LAT
Amperage (rated) |  |  |  |  | DX Coil WB EAT
DX Coil WB LAT
DX Coil Capacity
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
SGRD-1 | 9 | B | 6 | 75 |  |  | 0
SGRD-2 | 8 | B | 6 | 100 |  |  | 0
SGRD-3 | 12 | C | 12 | 540 |  |  | 0
|  |  |  | 715 |  | 0 | 0
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## EF (1)
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: EF- |  |  | Area:
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-090-VG |  |  | CFM | 520
Serial Num |  |  |  |  | Fan RPM | 1365
Type |  | CRE |  |  | RL Voltage | 115
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.25
Frame
Horsepower |  | 0.1
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 1.38
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EF-1 | SHOWERS | EG | 16X16 | 200 |  |  | 0
EF-1 | MEN | EG | 16X16 | 320 |  |  | 0
|  |  |  | 520 |  | 0.25 | 0.00048077
-

## EF (2)
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: EF- |  |  | Area:
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-080-VG |  |  | CFM | 380
Serial Num |  |  |  |  | Fan RPM | 1553
Type |  | CRE |  |  | RL Voltage | 115
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.25
Frame
Horsepower |  | 0.1
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 1.38
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EF-2 | WOMEN | EG | 10X10 | 240 |  |  | 0
EF-2 | JC | EG | 6X6 | 70 |  |  | 0
EF-2 | URINALYSIS | EG | 6X6 | 70 |  |  | 0
|  |  |  | 380 |  | 0.25 | 0.00065789
-

## EF (3)
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: EF-3 |  |  | Area: VAULTS
Unit Data |  |  |  |  | Test Data
MFG |  | GREENHECK |  |  |  | Design | Actual
Model Num |  | G-060-VG |  |  | CFM | 150
Serial Num |  |  |  |  | Fan RPM | 1449
Type |  | CRE |  |  | RL Voltage | 115
RL Amperage
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 0.125
Frame
Horsepower |  | 0.066
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 1.3
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
EF-3 | VAULT 120 | DUCT | 6X6 | 75 |  |  | 0
EF-3 | VAULT 122 | DUCT | 6X6 | 75 |  |  | 0
|  |  |  | 150 |  | 0.125 | 0.00083333
-

## EF (4)
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: EF-4 |  | Area: MECHANICAL ROOM 17
Unit Data |  |  | Test Data
MFG | GREENHECK |  |  | Design | Actual
Model Num | RCE3-20-313-VG |  | CFM | 500
Serial Num |  |  | Fan RPM | 1017
Type | PROP |  | RL Voltage | 115
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.25
Frame
Horsepower | 1
Motor Rpm | 1750
Phase | 1
Voltage (rated) | 115
Amperage (rated) | 10.3
Service Factor
-

## PAL02-EF- (1)
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: PAL02-EF-1 |  |  | Area:
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | USF-10 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | UTILITY SET |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame |  | 145T
Horsepower |  | 2 |  |  | Test Data
Motor Rpm |  | 3600 |  |  |  | Design | Actual
Phase |  | 3 |  |  | CFM | 1600
Voltage (rated) |  | 208 |  |  | Fan RPM | 3169
Amperage (rated) |  |  |  |  | RL Voltage | 208
Service Factor |  |  |  |  | RL Amperage
Discharge SP
Suction ESP
[5 empty] | Total ESP | 4
[5 empty] | Brake Horse Power | 1.76
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
PAL02-EF-1 | 202 | DUCT | 10 | 1600 |  |  | 0
#DIV/0!
#DIV/0!
-

## PAL02-EF- (2)
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: PAL02-EF-2 |  | Area:
Unit Data |  |  | Test Data
MFG | GREENHECK |  |  | Design | Actual
Model Num | AER-30 |  | CFM | 10000
Serial Num |  |  | Fan RPM | 1750
Type | PROP SIDEWALL |  | RL Voltage | 208
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.583
Frame |  |  | Brake Horse Power | 2.18
Horsepower | 2
Motor Rpm | 1750
Phase | 3
Voltage (rated) | 208
Amperage (rated)
Service Factor
-

## PAL02-EF- (3)
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: PAL02-EF-3 |  |  | Area: 203
Unit Data |  |  |  |  | Drive Data
MFG |  | GREENHECK |  |  | Motor Sheave Size
Model Num |  | BSQ-80 |  |  | Motor Bore Size
Serial Num |  |  |  |  | Fan Sheave Size
Type |  | INLINE |  |  | Fan Bore Size
Belt CL Distance
Motor Data |  |  |  |  | No of Belts
Motor MFG |  |  |  |  | Belt Size
Frame
Horsepower |  | 0.25 |  |  | Test Data
Motor Rpm |  | 1725 |  |  |  | Design | Actual
Phase |  | 1 |  |  | CFM | 200
Voltage (rated) |  | 115 |  |  | Fan RPM | 901
Amperage (rated) |  |  |  |  | RL Voltage | 115
Service Factor |  |  |  |  | RL Amperage
Discharge SP
Suction ESP
[5 empty] | Total ESP | 0.25
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
PAL02-EF-3 | 203 | DUCT | 8X8 | 200 |  |  | 0
#DIV/0!
#DIV/0!
-

## KEF (1)
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: KEF-1 |  | Area: GREASE HOOD
Unit Data |  |  | Test Data
MFG | CAPTIVE AIR |  |  | Design | Actual
Model Num | EADU180H |  | CFM | 1750
Serial Num |  |  | Fan RPM | 1024 | HZ
Type | PRV- UPBLAST |  | RL Voltage | 208
|  |  | RL Amperage | 6.6
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 1.25
Frame |  |  | Brake Horse Power | 0.78
Horsepower | 1.5
Motor Rpm
Phase | 3
Voltage (rated) | 208
Amperage (rated) | 6.6
Service Factor
-

## KEF (2)
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: KEF-2 |  | Area: HOT WELLS
Unit Data |  |  | Test Data
MFG | CAPTIVE AIR |  |  | Design | Actual
Model Num | EADU50H |  | CFM | 1275
Serial Num |  |  | Fan RPM | 1378 | HZ
Type | PRV- UPBLAST |  | RL Voltage | 208
|  |  | RL Amperage | 3.8
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP
Frame |  |  | Brake Horse Power | 0.296
Horsepower | 0.5
Motor Rpm
Phase | 1
Voltage (rated) | 208
Amperage (rated) | 3.8
Service Factor
-

## KEF (3)
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: KEF-3 |  | Area: DISH
Unit Data |  |  | Test Data
MFG | CAPTIVE AIR |  |  | Design | Actual
Model Num | EADU33H |  | CFM | 450
Serial Num |  |  | Fan RPM |  | HZ
Type | PRV- UPBLAST |  | RL Voltage | 208
|  |  | RL Amperage | 2.5
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.6
Frame |  |  | Brake Horse Power | 0.11
Horsepower | 0.33
Motor Rpm
Phase | 1
Voltage (rated) | 208
Amperage (rated) | 2.5
Service Factor
-

## MAU (01)
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: MAU-1 |  | Area: KH-1
Unit Data |  |  | Test Data
MFG | CAPTIVE AIR |  |  | Design | Actual
Model Num | EA1-D.500-15D |  | CFM | 1650
Serial Num |  |  | SF RPM | 1877
Type |  |  | RL Voltage | 208
Configuration |  |  | RL Amperage | 4.4
No. Filters / Size |  |  | Suction ESP
No. Filters / Size |  |  | Discharge ESP
|  |  | Total ESP | 0.57
Motor Data |  |  | Brake Horse Power | 1.03
Motor MFG
Frame
Horsepower | 1.5
Motor Rpm
Phase | 3
Voltage (rated) | 208
Amperage (rated) | 4.4
Service Factor

## MAU (2)
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: MAU-2 |  | Area: KH-2
Unit Data |  |  | Test Data
MFG | CAPTIVE AIR |  |  | Design | Actual
Model Num | EA1-D.500-15D |  | CFM | 1200
Serial Num |  |  | SF RPM | 1558
Type |  |  | RL Voltage | 115
Configuration |  |  | RL Amperage | 11.6
No. Filters / Size |  |  | Suction ESP
No. Filters / Size |  |  | Discharge ESP
|  |  | Total ESP | 0.59
Motor Data |  |  | Brake Horse Power | 0.568
Motor MFG
Frame
Horsepower | 1
Motor Rpm
Phase | 1
Voltage (rated) | 115
Amperage (rated) | 11.6
Service Factor

## KH-1
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: KH-1 |  | Area: GREASE HOOD
Unit Data |  |  | Test Data Supply
MFG | CAPTIVE AIR |  | AK factor
Model Num | 5424 EX-2-PSP-FS |  | Total AK Area
Job / Serial Num | 6119534 |  |  | PRELIM | FINAL
Type | CANOPY w/ PSP |  | Reading1 FPM
Hood Length | 106" |  | Reading2 FPM
Hood Width | 68" |  | Reading3 FPM
Supply Plenum Type | PSP |  | Reading4 FPM
Supply Plenum Width | 14" |  | Reading5 FPM
Supply Plenum Length | 106" / 68" |  | Reading6 FPM
Reading7 FPM
Test Data Exhaust |  |  | Reading8 FPM
Filter Type |  |  | Reading9 FPM
Filter Size 1 |  |  | Reading10 FPM
Filter Qty 1
Filter AK factor size 1
Filter Total AK Area 1
Filter Size 2 |  |  | Ave FPM(corr)
Filter Qty 2 |  |  | CFM | 1650
Filter AK factor size 2
Filter Total AK Area 2
| PRELIM | FINAL
Filter1 FPM
Filter2 FPM
Filter3 FPM
Filter4 FPM
Filter5 FPM
Filter6 FPM
Filter7 FPM
Filter8 FPM
Filter Ave FPM
CFM | 1750

## KH-2
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: KH-2 |  | Area: HOT WELLS
Unit Data |  |  | Test Data Supply
MFG | CAPTIVE AIR |  | AK factor
Model Num | 4824 ES-VHB-G-PSP-F-ND |  | Total AK Area
Job / Serial Num | 6119534 |  |  | PRELIM | FINAL
Type | CANOPY w/ PSP |  | Reading1 FPM
Hood Length | 102" |  | Reading2 FPM
Hood Width | 62" |  | Reading3 FPM
Supply Plenum Type | PSP |  | Reading4 FPM
Supply Plenum Width | 102" |  | Reading5 FPM
Supply Plenum Length | 14" |  | Reading6 FPM
Reading7 FPM
Test Data Exhaust |  |  | Reading8 FPM
Filter Type |  |  | Reading9 FPM
Filter Size 1 |  |  | Reading10 FPM
Filter Qty 1
Filter AK factor size 1
Filter Total AK Area 1
Filter Size 2 |  |  | Ave FPM(corr)
Filter Qty 2 |  |  | CFM | 1200
Filter AK factor size 2
Filter Total AK Area 2
| PRELIM | FINAL
Filter1 FPM
Filter2 FPM
Filter3 FPM
Filter4 FPM
Filter5 FPM
Filter6 FPM
Filter7 FPM
Filter8 FPM
Filter Ave FPM
CFM | 1275

## KH-3
National TAB
Project: USACE HVAC Reset
Address: Palatka, FL
Asset: KH-1 |  | Area: DISHWASHER
Unit Data |  |  | Test Data Exhaust
MFG | CAPTIVE AIR |  |  | DESIGN | ACTUAL
Model Num | 4824ES-VHB-G-ND |  | CFM | 450
Job / Serial Num | 6119534
Type
Hood Length | 48"
Hood Width | 48"