WAWA #8245 Yeagertown PRE-TAB Inspection

Item# (corresponds to number on MSET) and brief description

- Damper is not installed

- Transfer duct is not sized correctly Installed as 8”, supposed to be 10”

- Return Grille not correctly located, Is installed in retail ceiling grid needs to be in the ice chest ceiling grid

- Stuck damper handle, only closes halfway

- Flex duct is pinched on pluming support, tidy up the insulation

- Relocate start collar to the other side of the duct to prevent duct interference and pinching

- Multiple cases, long radius elbows were substituted for 90 Mitered elbows with turning vanes

- Elbow and damper not yet installed for exhaust grille

- Flip orientation of the linear diffuser for proper duct connection

- Duct drop is not a plenum drop and has a radiused elbow, seek engineer approval and or recommendation to repair

- Recommend reviewing and adjusting, Diffuser takeoff is not oriented the proper direction to connect to the linear diffuser, Plumbing is a major obstruction preventing proper orientation.

- Missing damper for return grille

- Return grille flex duct is excessive and needs to utilize more hard duct and flex needs to be better supported

- Start collar orientation is opposite of directional airflow (transition is not properly oriented) correct orientation and adjust damper position so it is still accessible.

- Start collar and duct is not installed, per MC they are trying to takeoff from the bottom of the supply trunk due to obstructions, Seek approval from engineer or recommendation for alternate solution.

- Duct takeoff is located further up on the main trunkline to avoid structure, Note only

- Note only, Keynote 9 has been done per prints, from experience at past wawa locations we have had a hard time getting airflow through the transition seemingly from turbulence causing higher Unit static pressure.

- Secure EF to curb

- Sink backdraft damper down, it is unable to open/needs to open fully.

- RTU setup/ gas piping/ Condensate lines/low voltage not yet completed at time of Pre-TAB inspection.