## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HOOD ON OA |  | HOOD OFF OA |  | HOOD ON EXHAUST |  | HOOD OFF EXHAUST
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU 1 | SALES | 800 | 818 | 350 | 378
RTU-2 | SALES | 800 | 783 | 350 | 378
RTU-3 | BOH/KITCHEN | 800 | 0 | 350 | 0
EF-1 | WOMEN'S RR |  |  |  |  | 225 | 215 | 225 | 215
EF-2 | MEN'S RR |  |  |  |  | 525 | 546 | 525 | 546
EF-3 | HOOD |  |  |  |  | 1350 | 1322 | 0 | 0
TOTALS |  | 2400 | 1601 | 1050 | 756 | 2100 | 2083 | 750 | 761
HOODS ON
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 2400 | 1601 |  |  | FRONT |  | -0.0048 |  | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 2100 | 2083 |  |  | SIDE |  | -0.0082
NET AIRFLOW |  | 300 | -482 |  |  | REAR |  | -0.0104 |  | TRUE
[6 empty] | AVERAGE |  | -0.0078
HOODS OFF
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20)
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 1050 | 756 |  |  | FRONT |  | -0.0032
TOTAL EXHAUST |  | 750 | 761 |  |  | SIDE |  | -0.0023
NET AIRFLOW |  | 300 | -5 |  |  | REAR |  | -0.0038
[6 empty] | AVERAGE |  | -0.0031
NOTES: