## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | Kitchen |  | 2060 | 0 | 1649 |  | 411 | #DIV/0! | 19.95%
RTU-2 | Dinning |  | 2932 | 0 | 2274 |  | 658 | #DIV/0! | 22.44%
RTU-3 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
MUA-1 | Hood 1 &Hood2 | [9 empty] | 2443
EF-1 | Fryer | [11 empty] | 1958
EF-2 | Grill | [11 empty] | 1631
EF-3 | Womens | [13 empty] | 62
TOTALS |  | 0 | 4992 | 0 | 3923 | 0 | 1069 |  |  | 0 | 2443 | 0 | 3589 | 0 | 62
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 0 | 3512 |  | FRONT |  | -0.0055 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 0 | 3651 |  | SIDE |  | -0.0069 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | -139 |  | REAR |  | -0.009 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0071333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0