## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | STORAGE | 1650 | 1628 | 1500 | 1480 | 150 | 148 | 9.091% | 9.091%
RTU-2 | WEST SALES | 2800 | 2808 | 2150 | 2135 | 650 | 673 | 23.21% | 23.97%
RTU-3 | EAST SALES | 2800 | 2837 | 2150 | 2163 | 650 | 674 | 23.21% | 23.76%
RTU-4 | SOUTH SALES | 3500 | 3390 | 2725 | 2613 | 775 | 777 | 22.14% | 22.92%
EF-1 | RESTROOM | [12 empty] | 75 | 75
EF-2 | RESTROOM | [12 empty] | 75 | 76
TOTALS |  | 10750 | 10663 | 8525 | 8391 | 2225 | 2272 |  |  | 0 | 0 | 0 | 0 | 150 | 151
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2225 | 2272 |  | FRONT |  | 0.0104 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 150 | 151 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 2075 | 2121 |  | REAR |  | 0.0075 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00895 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0