## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING |  | 657 |  | 405 |  | 252 | #DIV/0! | 38.36%
RTU-2 | KITHCEN/BOH |  | 2819 |  | 1957 |  | 862 | #DIV/0! | 30.58%
EF-1 | COOK LINE | [11 empty] | 2447
EF-2 | BATHROOM | [13 empty] | 31
EF-3 | BATHROOM | [13 empty] | 51
MAU-1 | HOOD-1 | [9 empty] | 996
TOTALS |  | 0 | 3476 | 0 | 2362 | 0 | 1114 |  |  | 0 | 996 | 0 | 2447 | 0 | 82
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 0 | 2110 |  | FRONT |  | -0.0322 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 0 | 2529 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | -419 |  | REAR |  | -0.02774 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.02997 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
MUA outlet does not connect to the hood plenum.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0