## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 |  |  | 5044 | 0 | 4553 |  | 491 | #DIV/0! | 9.734%
AC-2 |  |  | 5430 | 0 | 4720 |  | 710 | #DIV/0! | 13.08%
AC-3 | KITCHEN |  | 4409 | 0 | 3469 |  | 940 | #DIV/0! | 21.32%
AC-5 | PLAY AREA |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-6 | KITCHEN |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | FRYER HOOD | [11 empty] | 1075
EF-2 | GRILL HOOD LEFT | [11 empty] | 1042
EF-3 | GRILL HOOD RIGHT | [11 empty] | 1028
EF-4 | OVEN HOOD | [11 empty] | 617
EF-5 | RESTROOM | [13 empty] | 112
EF-6 | DISHWASHER FAN | [13 empty] | 396
TOTALS |  | 0 | 14883 | 0 | 12742 | 0 | 2141 |  |  | 0 | 0 | 0 | 3762 | 0 | 112
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 0 | 2141 |  | FRONT |  | -0.0259 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 0 | 3874 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | -1733 |  | REAR |  | -0.0777 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.0518 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390