## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | GENERAL SALES | 5040 | 1587 | 4340 | 1587 | 700 | 0 | 13.89% | 0%
RTU-2 | GENERAL SALES | 5040 | 2419 | 4340 | 1967 | 700 | 452 | 13.89% | 18.69%
RTU-3 | EMPLOYEE RM | 4200 | 0 | 3500 | 0 | 700 | 0 | 16.67% | #DIV/0!
RTU-4 | PHARMACY | 1680 | 964 | 1680 | 964 | 0 | 0 | 0% | 0%
EF-1 | ONE HR PHOTO | [12 empty] | 700 | 373
EF-2 | TOILET | [12 empty] | 500 | 338
EF-3 | EMPLOYEE RM | [12 empty] | 350 | 0
TOTALS |  | 15960 | 4970 | 13860 | 4518 | 2100 | 452 |  |  | 0 | 0 | 0 | 0 | 1550 | 711
[16 empty] | FALSE | FALSE | TRUE
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0 | FALSE | FALSE | TRUE
TOTAL OA |  | 2100 | 452 |  | FRONT |  | 0.0074
TOTAL EXHAUST |  | 1550 | 711 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0 | TRUE
NET AIRFLOW |  | 550 | -259 |  | REAR |  | 0.006
[5 empty] | AVERAGE |  | 0.0067 |  |  |  | DESIGN PRESSURIZATION IS >10% I(OA - EXH) / EXH > 10% |  |  |  | 1 | FALSE
[11 empty] | ACTUAL PRESSURIZATION IS >10% I(OA - EXH) / EXH > 10% |  |  |  | 0
NOTES:
RTU1: Economizer not functional & fan VFD not communicating with controller. RTU2: Motor sheave seems unstable, belt becomes loose around 54Hz, cannot speed up further. RTU3 is not functional. RTU4: Low cfm, no VFD single speed. EF1 & EF3 very dirty and clogged with debris, low cfm. EF2 not functional, speed controller not hooked up, no dial to turn.
DESIGN NET PRESSURIZATION CALCULATION
35.48%