## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 |  | 8750 | 8491 | 7000 | 6789 | 1750 | 1702 | 20% | 20.04%
AC-2 |  | 5250 | 5210 | 4350 | 4318 | 900 | 892 | 17.14% | 17.12%
AC-3 |  | 5250 | 5338 | 3650 | 3758 | 1600 | 1580 | 30.48% | 29.6%
AC-4 |  | 1875 | 1914 | 1375 | 1379 | 500 | 535 | 26.67% | 27.95%
AC-5 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-6 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 2014
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1315
EF-3 | RESTROOM | [12 empty] | 375 | 393
TOTALS |  | 21125 | 20953 | 16375 | 16244 | 4750 | 4709 |  |  | 0 | 0 | 3314 | 3329 | 375 | 393
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4750 | 4709 |  | FRONT |  | 0.0119 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3689 | 3722 |  | SIDE |  | 0.0034 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1061 | 987 |  | REAR |  | -0.0006 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0049 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390