## Sheet1
Summary
What was found initially: | Manager comments: Humidity issues, particularly in bar area (foggy windows, wet floors). Temperature is OK except for ba area when humidity spikes. 3-4 mecahnicals assessed equipment and fixed some issues, one hood had its exhaust fan motor replaced. Area around HDL1 (griddle hood) is hot and smoky while grilling.
Changes made: | Set OA damper positions on all RTUs. Increased EF1 to FLA. Decreased EF4 to new target. Building pressure improved from -0.050" to -0.023".
Air balancing & performance related issues that need to be resolved: | Adjust EF3 (utility exhaust fan) to new target if possible. May need to decrease MUA 2 to design if overall balance requires it. Units must be wired so that economizers close during unoccupied hours (currently all units are jumped to always run in Occupied). Humidity sensors must be wired in all RTUs, currently none are displaying a humidity reading and cannot run in dehumidification mode.
Air Balance Schedule
AIR GOING IN (+) | Target | Initial | Final
RTU-1 OA | 600 | 590 | 657
RTU-2 OA | 600 | 756 | 635 |  |  |  | Air Going In |  | Air Going out
RTU-3 OA | 1000 | 38 | 865 |  |  |  | 7619 |  | 8080
RTU-4 OA | 1200 | 210 | 1288
RTU-5 OA | 600 | 577 | 577
RTU-6 OA | 0 | NA | NA
MUA-1 | 2100 | 2256 | 2256
MUA-2 | 900 | 1341 | 1341
MUA-3 | 0 | NA | NA
AIR GOING OUT (-)
EF-1 | 1125 | 449 | 644
EF-2 | 1800 | 1869 | 1869 |  |  |  |  | Air Going In - Air Going out =
EF-3 | 1500 | 2471 | 2471 |  |  |  |  | -461
EF-4 | 1575 | 1797 | 1576
EF-5 | NA | NA | [5 empty] | Building Pressure Average:
EF-6 (DISH) | 0 | 1028 | 1028 |  |  |  |  | -0.023
EF-7 | NA | NA
RR Exhaust (EF-5) | 525 | 492 | 492
NET AIRFLOW (TARGET +200 CFM)
| 475 | -2338 | -461
Target Airflow Calculations
Unit | Tonnage | Target OA | OA %
RTU-1 | 7.5 | 600 | 20%
RTU-2 | 7.5 | 600 | 20%
RTU-3 | 12.5 | 1000 | 20%
RTU-4 | 15 | 1200 | 20%
RTU-5 | 7.5 | 600 | 20%
RTU-6 |  | 0 | N/A
Hoods | Served by | Served by | Type | Length (in) | Width (in) | MUA Type | Equipment 1 | Equipment 2 | Equipment 3 | CFM/ft1 | CFM/ft 2 | CFM/ft3 | CFM/ft Target | Target Exhaust | Target MUA
Hood 1L | EF-1 | MUA-1 | Type I | 60 | 51 | Short Cycle | Griddle - Flat Top |  |  | 225 | NOT FOUND | NOT FOUND | 225 | 1125 | 562.5
Hood 1R | EF-3 | MUA-1 | Type I | 120 | 51 | Short Cycle | Ovens |  |  | 150 | NOT FOUND | NOT FOUND | 150 | 1500 | 750
Hood 2 | EF-2 | MUA-2 | Type I | 96 | 51 | Short Cycle | Fryers |  |  | 225 | NOT FOUND | NOT FOUND | 225 | 1800 | 900
Hood 3 | EF-4 | MUA-1 | Type I | 84 | 51 | Short Cycle | Ovens | Fryers |  | 150 | 225 | NOT FOUND | 225 | 1575 | 787.5
Hood 4 | EF-6 | [8 empty] | NOT FOUND | NOT FOUND | NOT FOUND | 0 | 0 | #N/A
Restrooms | # of Toilets/Urinals | Target CFM
RR Exhaust (Total) | 7 | 525

## Kitchen Equipment
Equipment | CFM/ft
Char Grill | 275
Fryers | 225
Griddle - Flat Top | 225
Ovens | 150
Salamander | 275
Range | 200

## MUA Type
PSP | 0.8
Short Cycle | 0.5
Back Return | 0.5

## Sheet2
EF-1 | MUA-1 | Type I
EF-2 | MUA-2
EF-3 | MUA-3
EF-4
EF-5
EF-6
EF-7