## Sheet1
Summary
What was found initially: | Hoods were not exhausting required airflow. RTU's outdoor air was off of design.
Changes made: | RTU outdoor air was adjusted for proper airflow. RTU fan speeds were set to be constant across all fan speeds. EF-1 and EF-4 were asjusted for proper airflow.
Air balancing & performance related issues that need to be resolved: | EF-3's speed controller does not adjust the fan speed, neither does switching the speed dial to "OFF". EF-2 does not have a speed control dial installed.
Air Balance Schedule
AIR GOING IN (+) | Target | Initial | Final
RTU-1 OA | 520 | 938 | 1300 | 1250
RTU-2 OA | 520 | 734 | 1287 | 1250 |  |  | Air Going In |  | Air Going out
RTU-3 OA | 1040 | 1347 | 1101 | 1040 |  |  | 3688 |  | 5143
MUA-1 | 4147.5 | 1509
AIR GOING OUT (-)
EF-1 | 1200 | 1664 | 1248
EF-2 | 1687.5 | 849 | 899 |  |  |  |  | Air Going In - Air Going out =
EF-3 | 1050 | 1810 | 1810 |  |  |  |  | -1455
EF-4 | 1246.875 | 907 | 1186
EF-5 | 0 | [6 empty] | Building Pressure Average: | [5 empty] | Building Pressure:
EF-6 | 0 | [6 empty] | -0.19333 | [5 empty] | Front | -0.2
EF-7 | 0 | [12 empty] | Side | -0.19
RR Exhaust (Total) | 0 | [12 empty] | Back | -0.19
NET AIRFLOW (TARGET +200 CFM)
| 1043.125 | -702 | -1455
Target Airflow Calculations
Unit | Tonnage | Target OA | OA %
RTU-1 | 13 | 520 | 10%
RTU-2 | 13 | 520 | 10%
RTU-3 | 13 | 1040 | 20%
Hoods | Served by | Served by | Type | Length (in) | Width (in) | MUA Type | Equipment 1 | Equipment 2 | Equipment 3 | CFM/ft1 | CFM/ft 2 | CFM/ft3 | CFM/ft Target | Target Exhaust | Target MUA
Hood 1 | EF-1 | MUA-1 | Type I | 96 | 72 | PSP | Ovens |  |  | 150 | NOT FOUND | NOT FOUND | 150 | 1200 | 960
Hood 2 | EF-2 | MUA-1 | Type I | 90 | 66 | PSP | Griddle - Flat Top |  |  | 225 | NOT FOUND | NOT FOUND | 225 | 1687.5 | 1350
Hood 3 | EF-3 | MUA-1 | Type I | 84 | 66 | PSP | Ovens |  |  | 150 | NOT FOUND | NOT FOUND | 150 | 1050 | 840
Hood 4 | EF-4 | MUA-1 | Type I | 66.5 | 48 | PSP | Fryers |  |  | 225 | NOT FOUND | NOT FOUND | 225 | 1246.875 | 997.5
Restrooms | # of Toilets/Urinals | Target CFM
RR Exhaust (Total) |  | 0

## Kitchen Equipment
Equipment | CFM/ft
Char Grill | 275
Fryers | 225
Griddle - Flat Top | 225
Ovens | 150
Salamander | 275
Range | 200

## MUA Type
PSP | 0.8
Short Cycle | 0.5
Back Return | 0.5

## Sheet2
EF-1 | MUA-1 | Type I
EF-2 | MUA-2
EF-3 | MUA-3
EF-4
EF-5
EF-6
EF-7