## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | GEN. SALES | 2275 | 2220 | 1821 | 1778 | 454 | 442 | 19.96% | 19.91%
RTU-2 | FRONT SALES | 2625 | 2662 | 2101 | 2204 | 524 | 458 | 19.96% | 17.21%
RTU-3 | REAR SALES | 1750 | 1936 | 1400 | 1564 | 350 | 372 | 20% | 19.21%
RTU-4 | SALES | 2275 | 2351 | 1821 | 1941 | 454 | 410 | 19.96% | 17.44%
RTU-5 | PHARMACY | 1750 | 1649 | 1750 | 1649 | 0 | 0 | 0% | 0%
RTU-6 | RECEIVING | 1400 | 1523 | 1120 | 1254 | 280 | 269 | 20% | 17.66%
EF-1 | OFFICE | [12 empty] | 300 | 0
EF-2 | EMP.ROOM | [12 empty] | 300 | 0
EF-3 | MEN'S RR | [12 empty] | 300 | 241
EF-4 | WOMEN'S RR | [12 empty] | 300 | 264
EF-5 | PHOTO | [12 empty] | 750 | 435
TOTALS |  | 12075 | 12341 | 10013 | 10390 | 2062 | 1951 |  |  | 0 | 0 | 0 | 0 | 1950 | 940
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2062 | 1951 |  | FRONT |  | 0.0159 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1950 | 940 |  | SIDE |  | NA |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 112 | 1011 |  | REAR |  | 0.0102 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.01305 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0