## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | GEN. SALES | 2275 | 2220 | 1975 | 1898 | 300 | 322 | 13.19% | 14.5%
RTU-2 | FRONT SALES | 2625 | 2662 | 2225 | 2204 | 400 | 458 | 15.24% | 17.21%
RTU-3 | REAR SALES | 2275 | 2351 | 1975 | 2039 | 300 | 312 | 13.19% | 13.27%
RTU-4 | SALES | 1750 | 1936 | 1500 | 1675 | 250 | 261 | 14.29% | 13.48%
RTU-5 | PHARMACY | 1750 | 1649 | 1750 | 1649 | 0 | 0 | 0% | 0%
RTU-6 | RECEIVING | 1050 | 1132 | 980 | 1056 | 70 | 76 | 6.667% | 6.714%
EF-1 | OFFICE | [12 empty] | 300 | 303
EF-2 | EMP.ROOM | [12 empty] | 300 | 283
EF-3 | MEN'S RR | [12 empty] | 300 | 241
EF-4 | WOMEN'S RR | [12 empty] | 300 | 264
EF-5 | PHOTO | [12 empty] | 0 | 0
TOTALS |  | 11725 | 11950 | 10405 | 10521 | 1320 | 1429 |  |  | 0 | 0 | 0 | 0 | 1200 | 1091
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1320 | 1429 |  | FRONT |  | 0.0085 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1200 | 1091 |  | SIDE |  | NA |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 120 | 338 |  | REAR |  | NA | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0085 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0