## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | BOH | 1200 | 1226 | 1010 | 842 | 190 | 384 | 15.83% | 31.32%
RTU-2 | STOCK ROOM | 2500 | 2422 | 1925 | 1589 | 575 | 833 | 23% | 34.39%
RTU-3 | SALES | 2500 | 2453 | 1660 | 1614 | 840 | 839 | 33.6% | 34.2%
RTU-4 | SALES | 2500 | 2661 | 1660 | 2661 | 840 | 0 | 33.6% | 0%
RTU-5 | SALES | 2500 | 2619 | 1660 | 2619 | 840 | 0 | 33.6% | 0%
RTU-6 | SOLAR ZONE | 1200 | 1249 | 1200 | 1249 | 0 | 0 | 0% | 0%
EF-2 | RESTROOMS | [12 empty] | 275 | 285
TOTALS |  | 12400 | 12630 | 9115 | 10574 | 3285 | 2056 |  |  | 0 | 0 | 0 | 0 | 275 | 285
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3285 | 2056 |  | FRONT |  | 0.0054 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 275 | 285 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 3010 | 1771 |  | REAR |  | 0.0067 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00605 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0