## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3435 | 3125 | 3151 | 275 | 284 | 8.088% | 8.268%
RTU-2 | DINING | 2450 | 2501 | 1750 | 1762 | 700 | 739 | 28.57% | 29.55%
FCU-1 | MANAGERS OFFICE |  |  |  |  | 40 | 42 | #DIV/0! | #DIV/0!
MUA-1 | COOKLINE | [8 empty] | 1796 | 1852
KEF-1 | HD-1 | [10 empty] | 1385 | 1456
KEF-2 | HD-2 | [10 empty] | 860 | 905
EF-3 | RESTROOMS | [12 empty] | 150 | 153
TOTALS |  | 5850 | 5936 | 4875 | 4913 | 1015 | 1065 |  |  | 1796 | 1852 | 2245 | 2361 | 150 | 153
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2811 | 2917 |  | FRONT |  | 0.0191 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2395 | 2514 |  | SIDE |  | 0.0129 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 416 | 403 |  | REAR |  | 0.0158 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.015933 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2071 | 2136
TOTAL KITCHEN EXHAUST |  | 2245 | 2361
NET AIRFLOW |  | -174 | -225
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0